## Slide 1: Calculation of Power Systems Inertia and Frequency Response
Dino Porretta
Principal Engineer
ErgoSum Inc.
Steven Porretta
School of Computer Science
University of Carleton
http://ergosumweb.com/

## Slide 2: Introduction
Fundamental changes are taking place in the way that electricity is produced and consumed.
These changes are raising concerns about the deterioration of Inertial and Frequency Responses and the need to monitor them.
This paper presents a practical method to calculate the value of these Responses.
This paper focusses on generation losses. The concepts presented apply equally well to load losses.
End

## Slide 3: Data Requirements
System Frequency vs time curve following the loss of the generation.
The amount of generation lost.
The amount of generation just prior to the disturbance.
Question: Should (2.) and (3.) be measured in MW or MVA?
End
Leave question: MW or MVA

## Slide 4: System Quantities Calculated
M : Angular momentum.
D : Self regulation .
Edroop : Effective droop of governors.
Gat : Arrival time of the response from governors.
g(τ) : Governors response function.
End
Next: Basics concepts

## Slide 5: What Is Frequency Response ?
Frequency Response (FR) is the megawatt change in the Generation-Load imbalance affected by the system itself due to frequency changes alone.
FR derives from:
  Frequency characteristics of equipment.
  Generator governors.
  These two responses are fundamentally different.
End

## Slide 6: Equipment and Governor Frequency Responses
Equipment Frequency Response (EFR) is deployed with no delay as the frequency starts to change. Its magnitude is a result of equipment physics and design practices and it does not require changing input power to prime movers.
Governor Frequency Response (GFR) is deployed with a delay of about 2 to 5 seconds with full deployment 2 to 5 seconds later. Its magnitude is a result of governor Droop settings and generator loading practices and it does require changing input power to prime movers.
End
Next: Frequency response diagram

## Slide 7: EFR and GFR Model
End
Equation
Next: Beneficial FR or not

## Slide 8: Beneficial and Non-Beneficial EFR
Not all equipment provide beneficial EFR .
To be beneficial EFR has to oppose frequency change.
Question: Can a system without beneficial frequency response be operated?
End
Next: Inertial response

## Slide 9: What Is Inertial Response ?
This response is consistent with the following equation:
The left hand side of this equation represents the Inertial Response . At all times, the Inertial Response is equal to the accelerating power (Pa).
(2)
For a generation loss:
End
Equation
Next: Inertial response vs Frequency response

## Slide 10: Inertial Response Vs Frequency Response
Frequency Response reduces the accelerating power. Therefore:
  It decreases the rate of frequency decay
  It arrests the frequency decay
Inertial Response always matches the accelerating power. Therefore:
  Has no impact on the value at which frequency decay is arrested
  Higher M values decrease the rate of frequency decay
End
Next: Frequency Dev. Eq.

## Slide 11: The Frequency Deviation Equation
It can be shown that the frequency deviation due to a loss of generation ∆P is given by:
Where ∆f, ∆P, D, and M are in pu of:
P0 = Generation left in service at f0 .
f0 = Frequency at time zero plus.
Eq. (3) does not model governor response.
(3)
http://ergosumweb.com/
Next: Governor response function
Inertial Resp
FR Diagram
End

## Slide 12: Governor Response Model
End
Next: Incident data

## Slide 13: EI Generation Loss of 1711 MW, May/12/12
End
Next: FREDEV Program

## Slide 14: FREDEV Program

## Slide 15: Result Analysis
Governor frequency response lower than expected: Edroop 119%, response 240 MW.
Equipment frequency response higher than expected: D 3.65 pu, response of 1471 MW.
Governors frequency response arrives later than expected: 3.9 s to 23.9 s after disturbance.
System M of 13.65 s higher than that of highest inertia generator: due to the kinetic energy stored in motors.
There is evidence of governor response withdrawal: 20%, starting at 30 seconds.
End

## Slide 16: Conclusions
This paper has presented a method to calculate Inertia and Frequency Responses using data gathered for significant frequency events.
The calculations were done using the FREDEV program. This program is ideally suited for monitoring:
  Inertia and Frequency Responses.
  Inertia from motor loads.
  Adherence to governor settings guidelines.
  Governor response withdrawal practices.
  Optimize under-frequency protection settings.
End

## Slide 17: The End